## ASTM Testing Matrix
Category | ASTM Standard | Edition / Status | Field / Lab | Test / Evaluation | Primary Application | Typical Equipment | Pressure / Exposure | Water / Other Input | Typical Duration / Sequence | Primary Measurement | Acceptance / Use | Key Reporting Items
Air Leakage | ASTM E283/E283M | E283/E283M-26 | Laboratory | Fenestration air leakage | Windows; doors; curtain walls; skylights | Pressure chamber; airflow meter; pressure gauges | Project/product specified ΔP | N/A | Per standard | Air leakage rate | Project/product limit | Report ΔP, leakage, specimen, conditions
Air Leakage | ASTM E783 | E783-02(2018) | Field | Field air leakage | Installed windows and doors | Pressure chamber; airflow meter; pressure gauges | Project specified ΔP | N/A | Per procedure | Airflow rate | Project limit | Record test pressure and leakage location
Air Leakage | ASTM E1186 | E1186-22 | Field/Diagnostic | Air leakage site detection | Air barriers; walls; roofs; fenestration interfaces | Smoke; fog; IR; anemometer; pressure source | Induced pressure as appropriate | N/A | Investigation-specific | Leak location/path | Diagnostic; no universal pass/fail
Air Leakage | ASTM E2178 | E2178-21a | Laboratory | Air permeance of materials | WRBs; membranes; sheathing; air-barrier materials | Air-permeance apparatus | 75 Pa reference pressure | N/A | Per standard | L/s·m² | Project/material requirement | Report material conditioning and permeance
Air Leakage | ASTM E2357 | E2357-25 | Laboratory/Mock-up | Air leakage of air-barrier assemblies | Wall and roof air-barrier assemblies | Large pressure chamber; airflow instrumentation | Per standard/project | N/A | Includes conditioning | Assembly leakage | Project requirement | Report assembly configuration and conditioning
Air Leakage | ASTM E779 | E779-19 | Field | Whole-building air leakage | Single-zone/appropriately configured buildings | Blower fans; pressure gauges; airflow measurement | Multiple pressure points | N/A | Per standard | ACH / leakage rate | Project/code target | Pressurization/depressurization as applicable
Air Leakage | ASTM E1827 | E1827-22 | Field | Airtightness using orifice blower door | Small/single-zone buildings | Orifice blower door; pressure measurement | Multiple pressure points | N/A | Per procedure | ACH / leakage coefficient | Project requirement | Document building volume and test configuration
Air Leakage | ASTM E3158 | E3158-18 | Field | Large/multizone building airtightness | Large commercial/multizone buildings | Multiple fans; pressure/airflow measurement | Multiple pressure points | N/A | Per standard | Whole-building leakage | Project requirement | Document zone configuration and fan locations
Air Leakage | ASTM E3474 | Current edition to verify | Field | Individual test-zone air leakage | Multizone buildings | Fans; pressure taps; airflow measurement | Controlled zone pressure | N/A | Per standard | Zone leakage | Project requirement | Use for zonal performance verification
Air Leakage | ASTM E1258 | E1258-23 | Laboratory/Calibration | Fan pressurization device calibration | Blower-door/pressurization equipment | Calibration chamber; reference airflow instrumentation | Calibration range | N/A | Per standard | Fan airflow accuracy | Calibration tolerance | Maintain calibration certificate
Air Exchange | ASTM E741 | Current edition to verify | Field | Air-change rate using tracer gas | Buildings / zones | Tracer gas; gas analyzer; data logger | Per procedure | N/A | Decay/constant concentration method | ACH | Project-specific | Document gas, sampling and environmental conditions
Water Penetration | ASTM E1105 | E1105-15(2023) | Field | Water penetration of installed fenestration | Windows; curtain walls; storefront; doors; skylights | Pressure chamber; spray rack; pressure gauge; flow measurement | Project specified ΔP | Calibrated spray rack | Per procedure | No uncontrolled water penetration | Record pressure, spray, duration, leakage
Water Penetration | ASTM E331 | E331-00(2023) | Laboratory | Water penetration under uniform static pressure | Windows; curtain walls; doors; skylights | Pressure chamber; spray rack | Project/product specified ΔP | Calibrated spray system | Per standard | No water penetration beyond criterion | Laboratory specimen report
Water Penetration | ASTM E547 | E547-00(2024) | Laboratory | Water penetration under cyclic pressure | Fenestration; curtain walls | Pressure chamber; spray system | Cyclic pressure sequence | Calibrated spray system | Per standard | No unacceptable water penetration | Pressure history and leakage
Water Penetration | ASTM E2268 | Current edition to verify | Laboratory | Water penetration using rapid/pulsed pressure | Fenestration | Pressure chamber; spray equipment | Rapid/pulsed pressure | Calibrated spray system | Per standard | Project/product criterion | Verify edition before specification
Wall Leakage Investigation | ASTM E2128 | E2128-26 | Field/Diagnostic | Evaluation of water leakage through building walls | Exterior walls; façade assemblies; interfaces | Spray equipment; chamber; probes; moisture meters; borescope | Investigation-specific | Investigation-specific | Investigation-specific | Leak source/path determination | Document diagnostic sequence and findings
Masonry Water | ASTM C1601 | C1601-22a | Field | Surface water penetration of masonry | Brick; CMU; masonry walls | Masonry chamber; water supply; flow measurement | Per standard | Controlled water flow | Per standard | Project/comparative criterion | Do not equate with E514 results
Masonry Water | ASTM E514/E514M | E514/E514M-20 | Laboratory | Water penetration and leakage through masonry | Masonry wall specimens | Wind-driven rain apparatus; pressure chamber | Standard-defined | Wind-driven rain | Per standard | Project/lab criterion | Report leakage and specimen conditions
Structural | ASTM E330/E330M | E330/E330M-21 | Laboratory/Mock-up | Structural performance under uniform static pressure | Windows; curtain walls; doors; skylights | Pressure chamber; displacement gauges | Design/project pressure | N/A | Per standard | Deflection/permanent deformation/failure | Record positive/negative pressures
Structural | ASTM E1233/E1233M | Current edition to verify | Laboratory/Mock-up | Structural performance under cyclic pressure | Fenestration; curtain walls; doors | Pressure chamber; displacement instrumentation | Cyclic positive/negative pressure | N/A | Per standard | Structural performance | Document pressure sequence
Impact | ASTM E1886 | Current edition to verify | Laboratory/Mock-up | Impact and cyclic pressure | Hurricane-resistant fenestration | Missile launcher; pressure chamber | Per standard/project | Specified missile | Per standard | No failure beyond criteria | Report impact location, velocity and pressure
Impact | ASTM E1996 | E1996-26 | Laboratory/Mock-up | Windborne debris impact | Windows; curtain walls; doors; impact protection | Missile impact apparatus; pressure chamber | Per standard/project | Specified missile | Per standard | Impact/pressure performance | Coordinate with applicable code/approval
Metal Roofing | ASTM E1646 | Current edition to verify | Laboratory/Mock-up | Water penetration of metal roof panels | Metal roof systems | Roof test chamber; spray system; pressure system | Uniform static pressure | Water spray | Per standard | No leakage beyond criterion | Document roof assembly and pressure
Metal Roofing | ASTM E2140 | E2140-01(2023) | Laboratory/Mock-up | Water penetration by static water head | Metal roof panels | Water-head apparatus | Static water head | Water head | Per standard | No leakage beyond criterion | Document head height/duration
Metal Roofing | ASTM E1680 | Current edition to verify | Laboratory/Mock-up | Air leakage of exterior metal roof systems | Metal roof systems | Pressure chamber; airflow measurement | Specified ΔP | N/A | Per standard | Air leakage | Project/system limit
Metal Roofing | ASTM E1592 | Current edition to verify | Laboratory/Mock-up | Structural performance of sheet-metal roof/siding | Metal roofs/walls | Pressure chamber; displacement gauges | Uniform static pressure | N/A | Per standard | Deflection/failure | Record pressure and deformation
Thermal | ASTM C1363 | Current edition to verify | Laboratory | Thermal performance using hot box | Walls; roofs; composite enclosure assemblies | Hot-box apparatus | Controlled temperature differential | N/A | Steady state | U-value / thermal resistance | Report boundary conditions and specimen
Thermal | ASTM C1199 | Current edition to verify | Laboratory | Steady-state thermal transmittance of fenestration | Windows/doors/fenestration | Hot-box apparatus | Steady-state temperature difference | N/A | Steady state | U-factor | Report frame/glazing configuration
Thermal | ASTM E1423 | Current edition to verify | Laboratory | Thermal transmittance of fenestration | Windows; curtain walls; doors | Hot-box apparatus | Steady-state conditions | N/A | Per standard | Thermal transmittance | Document specimen and boundary conditions
Vapor | ASTM E96/E96M | Current edition to verify | Laboratory | Water vapor transmission | Membranes; coatings; building materials | Desiccant/water method apparatus | Controlled vapor pressure/RH differential | N/A | Per method | Permeance / transmission | State method and test conditions
Sealants | ASTM C1521 | Current edition to verify | Field | Field adhesion of sealants | Exterior sealant joints | Adhesion-test tools; hand tools | Pull/adhesion load | N/A | Field-specific | Adhesive/cohesive failure | Record substrate, sealant, primer, failure mode
Sealants | ASTM C719 | Current edition to verify | Laboratory | Adhesion/cohesion under cyclic movement | Elastomeric joint sealants | Movement cycling apparatus | Specified movement cycles | N/A | Per standard | Adhesion/cohesion | Report movement class and failures
Sealants | ASTM C794 | Current edition to verify | Laboratory | Adhesion-in-peel | Sealants | Peel-test apparatus | Per standard | N/A | Per standard | Adhesion force/failure | Report substrate and failure mode
Sealants | ASTM C1087 | Current edition to verify | Laboratory | Sealant/accessory compatibility | Sealants; primers; spacers; membranes; substrates | Conditioning and test apparatus | Per standard | N/A | Per standard | Compatibility | Evaluate adhesion/staining/other effects
Sealants | ASTM C1248 | Current edition to verify | Laboratory | Staining of porous substrates by sealants | Stone; masonry; porous substrates | Conditioning/test apparatus | Per standard | N/A | Per standard | Staining | Report substrate and sealant configuration
Sealants | ASTM C1184 | Current edition to verify | Laboratory | Structural silicone sealants | Structural glazing | Tensile/adhesion equipment | Per standard | N/A | Per standard | Structural adhesion/performance | Coordinate with glazing system requirements
EIFS | ASTM E2485/E2485M | E2485/E2485M-26 | Laboratory | Freeze/thaw resistance | EIFS / EIFS with drainage | Environmental chamber; conditioning equipment | Freeze/thaw cycles | Water conditioning | Per standard | No unacceptable deterioration | Document assembly and cycles
Façade Evaluation | ASTM E1825 | Current edition to verify | Field/Diagnostic | Exterior enclosure evaluation | Façades; enclosure materials/systems | Visual/physical inspection tools; testing equipment | Investigation-specific | N/A | Investigation-specific | Condition/performance evaluation | Photo documentation and repair recommendations
Façade Inspection | ASTM E2270 | Current edition to verify | Field | Periodic façade inspection | Existing building façades | Visual/physical inspection equipment | Inspection-specific | N/A | Per standard | Unsafe condition identification | Document observed distress and locations
BECx | ASTM E2813 | E2813-26 | Field/Project Process | Building enclosure commissioning | New construction / major renovation | Project-specific testing equipment | Per OPR/BOD/test plan | Project-specific | Commissioning plan | OPR/BOD performance requirements | Include testing, deficiencies and closeout
Hygrothermal | ASTM E3054/E3054M | E3054/E3054M-23 | Analysis | Hygrothermal modeling/characterization | Wall/roof assemblies | Hygrothermal modeling software | Climate/material/boundary conditions | N/A | Per modeling methodology | Temperature/moisture performance | Document assumptions and inputs

## 1. Air Leakage Airtightness
ASTM Standard | Title / Application | Typical Use
ASTM E283/E283M-26 | Rate of Air Leakage Through Exterior Windows, Skylights, Curtain Walls, and Doors | Laboratory fenestration air leakage | ASTM specifically distinguishes material air permeance (E2178), assembly air leakage (E2357), and constructed-building air leakage (E3158), which is an important distinction when developing an enclosure testing program.
ASTM E783 | Field Measurement of Air Leakage Through Installed Exterior Windows and Doors | Field testing windows/doors | Particularly important for your type of work, that covers everything from finding individual air leaks through material, assembly, fenestration, zone, and whole-building testing.
ASTM E1186-22 | Air Leakage Site Detection in Building Envelopes and Air Barrier Systems | Smoke, pressure, tracer techniques for locating leaks | E1186 → E2178 → E2357 → E783 → E779/E1827 → E3158/E3474
ASTM E2178-21a | Air Leakage Rate and Air Permeance of Building Materials | Air-barrier material testing
ASTM E2357-25 | Air Leakage Rate of Air Barrier Assemblies | Wall/air-barrier assembly testing
ASTM E779-19 | Air Leakage Rate by Fan Pressurization | Whole-building airtightness
ASTM E1827-22 | Airtightness of Buildings Using an Orifice Blower Door | Building/zone airtightness
ASTM E3158-24 | Air Leakage Rate of a Large or Multizone Building | Large/multizone whole-building testing
ASTM E3474-25 | Air Leakage Rate of Building Envelope of an Individual Test Zone within a Multizone Building | Zonal/multizone testing
ASTM E1258-23 | Airflow Calibration of Fan Pressurization Devices | Blower-door/fan calibration

## 2. Water Penetration
ASTM Standard | Application (Windows, Curtain Wall & Fenestration)
ASTM E331-00(2023) | Water penetration of windows, skylights, doors and curtain walls under uniform static pressure | The key distinction is: E331 = laboratory water testing E1105 = field water testing E547 = cyclic pressure water testing E2268 = rapid/pulsed pressure water testing ASTM E1105 specifically covers installed exterior windows, skylights, doors and curtain walls, including testing of joints between assemblies and adjacent construction.
ASTM E1105-15(2023) | Field water penetration testing of installed windows, skylights, doors and curtain walls
ASTM E547-00(2024) | Water penetration under cyclic static air pressure
ASTM E2268-04(2023) | Water penetration using rapid pulsed air pressure
ASTM E283/E283M-26 | Air leakage through windows, skylights, curtain walls and doors
ASTM E783 | Field air leakage through installed windows and doors
ASTM E330/E330M-21 | Structural performance under uniform static air pressure
ASTM E1233/E1233M-21 | Structural performance under cyclic air pressure

## 3. Fenestration Air Leakage
ASTM Standard | Application | Field / Lab
ASTM E283/E283M-26 | Determination of air leakage through: windows,skylights,curtain walls,doors | Laboratory | It is the primary laboratory air-leakage test under specified pressure differences.
ASTM E1424-22 | Air leakage through windows, skylights, curtain walls and doors under specified pressure and temperature differences. | Laboratory
ASTM E783 | Field measurement of air leakage through installed exterior windows and doors. | Field
ASTM E2319-22 | Component/Interface | Laboratory/Diagnostic | Determines airflow through the face and sides of exterior windows, curtain walls and doors. It is essentially a modified E283 approach intended to help characterize air leakage paths within the fenestration system.

## 4. Structural Performance
ASTM Standard | Application | Field / Lab
E330/E330M-21 | Uniform static pressure structural testing | Laboratory/Mock-up | ASTM E330/E330M is particularly important for curtain wall mock-up testing. It evaluates structural performance of exterior windows, doors, skylights and curtain walls under uniform static pressure.
E1233/E1233M-21 | Cyclic air pressure structural testing | Laboratory/Mock-up
E1886-19 | Missile impact + cyclic pressure | Laboratory/Mock-up
E1996-26 | Windborne debris/hurricane fenestration | Laboratory
E2264-24 | Temperature cycling of fenestration products | Laboratory/Mock-up

## Quick Selection Guide
Enclosure Component | Discipline | Primary ASTM | Purpose
Windows / Storefront / Curtain Wall | Air | E783 | Field air leakage
Windows / Storefront / Curtain Wall | Water | E1105 | Field water penetration
Windows / Curtain Wall | Structural | E330/E330M | Static pressure structural
Air Barrier Material | Air | E2178 | Material air permeance
Air Barrier Assembly | Air | E2357 | Assembly air leakage
Whole Building | Air | E779 / E1827 / E3158 | Whole-building airtightness
Existing Leaking Wall | Water/Diagnostic | E2128 | Leakage investigation
Brick / CMU | Water | C1601 | Field masonry surface penetration
Masonry Mock-up | Water | E514/E514M | Laboratory through-wall leakage
Metal Roof | Water | E1646 / E2140 | Water penetration
Sealant Joint | Adhesion | C1521 | Field adhesion
Building Enclosure Commissioning | BECx | E2813 | Commissioning framework

## Sheet1
Enclosure Component | Air | Water | Structural | Diagnostic | Recommended Primary ASTM
Curtain wall | ✓ | ✓ | ✓ | ✓ | E783, E1105, E330
Storefront | ✓ | ✓ | ✓ | ✓ | E783, E1105, E330
Window wall | ✓ | ✓ | ✓ | ✓ | E783, E1105, E330
Windows | ✓ | ✓ | ✓ | ✓ | E783, E1105, E330
Exterior doors | ✓ | ✓ | ✓ | — | E783, E1105
Skylights | ✓ | ✓ | ✓ | ✓ | E283/E783, E331/E1105, E330
ACM/MCM façade | — | ✓ | ✓ | ✓ | E2128 + project-specific testing
Fiber-cement cladding | — | ✓ | — | ✓ | E2128 + project-specific testing
Brick veneer | — | ✓ | — | ✓ | C1601 / E514/E514M / E2128
CMU | — | ✓ | — | ✓ | C1601 / E514/E514M
EIFS | — | ✓ | — | ✓ | E2128 / E2485
Stucco | — | ✓ | — | ✓ | E2128 + project-specific testing
Air barrier | ✓ | — | — | ✓ | E2178 / E2357 / E1186
WRB | ✓ | ✓ | — | ✓ | E2178 / E2357 / E2128
Roof membrane | ✓* | ✓ | — | ✓ | E2128 / system-specific ASTM
Metal roof | ✓ | ✓ | ✓ | ✓ | E1680 / E1646 / E2140 / E1592
Sealants | — | ✓* | — | ✓ | C1521 / C719 / C794
Whole building | ✓ | — | — | ✓ | E779 / E1827 / E3158 / E3474
Building enclosure BECx | ✓ | ✓ | ✓ | ✓ | E2813 + applicable test methods

## Sheet2
Test | Standard | Pressure | Water Application | Typical Duration | Primary Observation | Reporting
Fenestration field water test | E1105 | Project-specified ΔP | Calibrated spray rack | Per Procedure A/B | Interior water penetration | Test pressure, spray rate, duration, leakage location
Fenestration laboratory water | E331 | Project-specified ΔP | Calibrated spray rack | Standard procedure | Water penetration | Pressure, spray rate, duration, failure location
Cyclic water test | E547 | Project-specified cyclic ΔP | Calibrated spray rack | Standard cycle sequence | Water penetration during cycles | Pressure history + leakage
Field fenestration air | E783 | Project-specified ΔP | N/A | Multiple pressure points | Airflow rate | L/s·m² or CFM/ft²
Laboratory fenestration air | E283 | Specified ΔP | N/A | Multiple pressure points | Air leakage | Leakage vs. pressure
Air-barrier material | E2178 | Reference 75 Pa | N/A | Per procedure | Air permeance | L/s·m² @ 75 Pa
Air-barrier assembly | E2357 | Per standard | N/A | Includes conditioning | Assembly leakage | Air leakage rating
Whole-building airtightness | E779 | Multiple ΔP | N/A | Pressurization/depressurization | Building airflow | ACH, CFM, L/s·m²
Blower-door | E1827 | Multiple ΔP | N/A | Single-/two-point | Building leakage | Leakage coefficient / ACH
Large/multizone | E3158 | Multiple ΔP | N/A | Per procedure | Building/zone leakage | Zone/building leakage
Air leakage diagnosis | E1186 | Usually induced ΔP | N/A | Investigation-specific | Location of leaks | Photo/thermal/smoke documentation
Masonry field | C1601 | Standard-defined | Standard-defined flow | Per procedure | Surface water penetration | Water penetration rate
Masonry laboratory | E514/E514M | Standard-defined | Wind-driven rain | Per procedure | Through-wall leakage | Water collected/leakage
Metal roof water | E1646 | Specified ΔP | Water spray | Per standard | Leakage | Location and quantity
Metal roof water head | E2140 | Water head | Static head | Per standard | Leakage | Leakage location
Structural fenestration | E330/E330M | Design/project pressure | N/A | Per pressure sequence | Deflection/failure | Deflection + permanent deformation
Sealant adhesion | C1521 | Pull/adhesion load | N/A | Field-specific | Adhesive/cohesive failure | Location, substrate, failure mode
Whole-building air calibration | E1258 | Calibration range | N/A | Calibration procedure | Fan airflow accuracy | Calibration curve/certificate

## Sheet3
Category | ASTM Standard | Current Edition | Test / Evaluation | Primary Application | Typical Equipment | Key Test Parameters | Typical Acceptance Criterion
Water – Fenestration | E1105 | E1105-15(2023) | Field water penetration | Windows, curtain walls, storefront, skylights, doors | Pressure chamber, calibrated spray rack, pressure gauge, water-flow measurement | Uniform or cyclic pressure; water spray; pressure specified by project | No uncontrolled water penetration to interior or defined failure location
Water – Fenestration | E331 | E331-00(2023) | Water penetration under uniform static pressure | Laboratory windows, curtain walls, storefront, doors, skylights | Test chamber, spray rack, calibrated nozzles, pressure measurement | Uniform static pressure; water spray | No water penetration beyond defined failure criteria
Water – Fenestration | E547 | E547-00(2024) | Water penetration under cyclic pressure | Laboratory fenestration and curtain walls | Pressure chamber and calibrated spray system | Cyclic static pressure | No water penetration beyond specified limit
Water – Fenestration | E2268 | Current active edition to be confirmed before specification | Water penetration using rapid/pulsed pressure | Specialized fenestration testing | Pressure chamber, spray equipment | Rapid/pulsed pressure cycles | Project-specific
Water – Field Diagnostic | E2128 | E2128-26 | Investigation of water leakage | Building walls, façade interfaces, leakage investigations | Hose/nozzle, chamber, probes, moisture meters, borescope, etc. | Investigation methodology rather than one prescribed pressure | Determination of leakage source/path and wall performance
Water – Masonry | C1601 | C1601-22a | Field water penetration of masonry surface | Brick, CMU, stone and masonry walls | Masonry chamber, water supply, flow measurement, pressure instrumentation | Controlled water flow and air pressure | Project-specific / comparative results
Water – Masonry | E514/E514M | E514/E514M-20 | Water penetration and leakage through masonry | Laboratory masonry wall specimens | Wind-driven rain apparatus, pressure chamber, collection system | Controlled wind-driven rain and pressure | Project-specific; comparative performance
Water – Masonry Drainage | C1715/C1715M | C1715/C1715M-22 | Masonry wall drainage-system leakage/performance | Cavity walls and drainage systems | Test apparatus appropriate to drainage system | Per standard | Project/specification dependent
Air – Fenestration | E783 | E783-02(2018) | Field air leakage | Installed windows and doors | Pressure chamber, calibrated airflow meter, pressure gauge | Specified pressure differential | Air leakage ≤ project limit
Air – Fenestration | E283/E283M | E283/E283M-26 | Laboratory air leakage | Windows, curtain walls, skylights, doors | Test chamber, airflow measurement, pressure measurement | Specified pressure differential | Air leakage ≤ product/specification limit
Air – Fenestration | E1424 | E1424-22 | Air leakage with temperature differential | Windows, curtain walls, doors | Environmental/test chamber, airflow measurement | Pressure + temperature differential | Product/specification dependent
Air – Fenestration | E2319 | E2319-22 | Airflow through face and sides | Windows, curtain walls and doors | Test chamber, airflow measurement | Controlled pressure differential | Used to identify/quantify leakage through specific portions
Air – Building Material | E2178 | E2178-21a | Air permeance of building materials | WRBs, membranes, sheathing, panels, air-barrier materials | Air-permeance chamber, pressure measurement, airflow measurement | Reference ΔP = 75 Pa | Material air permeance requirement
Air – Assembly | E2357 | E2357-25 | Air leakage of air-barrier assemblies | Wall/roof air-barrier assemblies and mock-ups | Large test chamber, pressure measurement, airflow measurement | Pressure differential + conditioning cycles | Assembly leakage rating / project criterion
Air – Whole Building | E779 | E779-19 | Whole-building air leakage by fan pressurization | Single-zone buildings / larger buildings configured appropriately | Blower fans, pressure gauges, airflow measurement | Multiple pressure points; pressurization/depressurization | ACH, CFM, L/s·m² or project requirement
Air – Whole Building | E1827 | E1827-22 | Building airtightness using orifice blower door | Small/single-zone buildings | Orifice blower door, pressure measurement | Single- or two-point method | Building airtightness parameter
Air – Large/Multi-Zone | E3158 | E3158-18 | Air leakage of large or multizone building | Large commercial buildings | Multiple fans, pressure measurement, airflow measurement | Multi-zone pressure testing | Project-specific whole-building leakage
Air – Zone | E3474 | Verify current edition before specification | Air leakage of individual test zones | Multizone buildings | Fans, pressure taps, airflow measurement | Controlled zone pressure | Project-specific
Air – Leak Detection | E1186 | E1186-22 | Air-leakage site detection | Walls, roofs, air barriers, fenestration interfaces | Smoke, theatrical fog, IR camera, anemometer, sound, tracer techniques | Usually performed under controlled pressure | Identification/location of leakage paths
Air – Fan Calibration | E1258 | E1258-23 | Calibration of fan pressurization devices | Blower-door / whole-building testing | Calibration chamber, reference airflow instrumentation | Multiple airflow ranges | Calibration within required accuracy
Air – Air Exchange | E741 | Verify current edition | Tracer-gas air-change measurement | Building ventilation / natural air exchange | Tracer gas, gas analyzer, data logger | Concentration decay or constant concentration | ACH / air-change performance
Structural – Fenestration | E330/E330M | E330/E330M-21 | Structural performance under uniform static pressure | Windows, curtain walls, doors, skylights | Structural test chamber, pressure system, displacement gauges | Positive/negative static pressure | No structural failure / permanent deformation beyond specified limit
Structural – Fenestration | E1233/E1233M | Verify current edition | Structural performance under cyclic pressure | Windows, curtain walls, doors | Pressure chamber, displacement instrumentation | Cyclic positive/negative pressure | Project-specific structural criteria
Impact / Hurricane | E1886 | Current active edition | Impact + cyclic pressure | Hurricane-resistant fenestration | Missile launcher, pressure chamber | Impact followed by cyclic pressure | No failure beyond standard-defined criteria
Impact / Hurricane | E1996 | E1996-26 | Windborne debris impact performance | Windows, curtain walls, doors, impact protection | Missile impact apparatus + pressure chamber | Missile size/velocity + cyclic pressure | Standard/project-specific impact criteria
Metal Roofing – Water | E1646 | Current active edition | Water penetration of metal roof panels | Metal roof systems | Roof test chamber, water spray, pressure system | Uniform static pressure + water | No water penetration
Metal Roofing – Water | E2140 | E2140-01(2023) | Water penetration by static water head | Metal roof panels | Water head apparatus | Static water head | No leakage beyond criteria
Metal Roofing – Air | E1680 | Current active edition | Air leakage of exterior metal roof systems | Metal roof assemblies | Pressure chamber, airflow measurement | Specified pressure differential | Air leakage ≤ project limit
Metal Roofing – Structural | E1592 | Current active edition | Structural performance of sheet-metal roof/siding | Metal roof and wall systems | Pressure chamber, displacement gauges | Uniform static pressure | Deflection / failure criteria
Thermal – Assembly | C1363 | Current active edition | Thermal performance using hot box | Walls, roofs and enclosure assemblies | Guarded/hot-box apparatus | Controlled temperature differential | U-value / thermal resistance
Thermal – Fenestration | C1199 | Current active edition | Thermal transmittance of fenestration | Windows and doors | Hot-box apparatus | Steady-state temperature difference | U-factor / thermal transmittance
Thermal – Fenestration | E1423 | Current active edition | Thermal transmittance of fenestration | Windows, curtain walls, doors | Hot-box apparatus | Steady-state conditions | Thermal transmittance
Vapor | E96/E96M | Current active edition | Water vapor transmission | Membranes, coatings, materials | Desiccant/water method apparatus | Controlled RH / vapor pressure differential | Permeance / vapor transmission
Sealant | C1521 | Current active edition | Field adhesion of sealants | Exterior sealant joints | Hand tools, adhesion-test equipment | Pull/adhesion evaluation | Cohesive/adhesive performance per specification
Sealant | C719 | Current active edition | Adhesion/cohesion under cyclic movement | Elastomeric sealants | Movement cycling apparatus | Specified movement cycles | No adhesive/cohesive failure beyond criteria
Sealant | C794 | Current active edition | Adhesion-in-peel | Sealants | Peel-test equipment | Controlled peel test | Minimum adhesion
Sealant | C1087 | Current active edition | Compatibility testing | Sealant/accessory materials | Laboratory conditioning/testing | Compatibility exposure | No unacceptable staining, adhesion loss, etc.
Sealant | C1248 | Current active edition | Staining of porous substrates | Sealant/masonry/stone | Test specimens, conditioning chamber | Exposure/conditioning | No unacceptable staining
Sealant | C1184 | Current active edition | Structural silicone sealants | Structural glazing | Laboratory tensile/adhesion equipment | Per standard | Structural performance criteria
EIFS | E2485/E2485M | E2485/E2485M-26 | Freeze/thaw resistance | EIFS and EIFS with drainage | Environmental chamber, water conditioning | Freeze/thaw cycles | No unacceptable deterioration
Façade Investigation | E1825 | Current active edition | Exterior enclosure evaluation | Façade condition assessments | Visual, probes, moisture meters, testing equipment | Investigation-specific | Condition/performance evaluation
Façade Investigation | E2270 | Current active edition | Periodic façade inspection | Existing building façades | Visual/physical inspection equipment | Inspection protocol | Unsafe-condition identification
Enclosure Commissioning | E2813 | E2813-26 | Building enclosure commissioning | New construction / major renovation | Project-specific testing equipment | Commissioning plan / performance testing | OPR/BOD/project requirements
Hygrothermal Analysis | E3054/E3054M | E3054/E3054M-23 | Characterization/use of hygrothermal models | Walls, roofs and enclosure assemblies | WUFI or equivalent modeling software | Climate, materials, boundary conditions | Project-specific moisture/thermal criteria

## Notes
There is no single ASTM category called “Building Enclosure Testing.” The applicable standards are distributed among ASTM Committees E06 (Performance of Buildings), C15 (Masonry), C16 (Thermal Insulation), C24 (Building Seals and Sealants), and others. Also, ASTM is only part of the enclosure-testing landscape. For the type of work you do, a complete testing reference library would normally also include AAMA/FGIA, ASTM, NFRC, ANSI, CSA, ABAA, and sometimes ICC/IBC requirements. In particular, AAMA/FGIA standards are extremely important for fenestration and curtain-wall testing, while ASTM provides many of the underlying test methods.
If your goal is a professional Building Enclosure Testing Matrix, a table of ASTM number → current edition → test method → equipment required → test pressure → water application rate → test duration → applicable enclosure system → field/lab → pass/fail criteria.